## 电缆规格型号及预估长度
序号 | 电缆型号及规格 | 电缆长度(米） | 用途 | 备注
1 | ZRC-YJVR-3*4+1*2.5 | 1230 | 电动阀门动力电缆
2 | ZRC-YJVR-4*2.5 | 40542 | 电动阀门动力电缆,仪表电源电缆
3 | ZRC-YJVR-2*4 | 5015 | 保温箱电源电缆
4 | ZRC-YJVR-2*1.5 | 8410 | 仪表电源电缆
5 | ZRC-DJVVP1R-1*2*1.0 | 41813 | 压力变送器,温度变送器变送器,压力开关,液位开关用
6 | ZRC-DJVVP1R-2*2*1.0 | 7326 | 调节阀，电机轴承温度，风机轴承温度用
7 | ZRC-DJVVP1R-4*2*1.0 | 7638 | 电机线圈温度用
8 | ZRC-DJVVR-5*2*1.0 | 32000 | 电动门控制信号用
9 | ZRC-DJVVR-7*2*1.0 | 3137 | 就地控制箱及给煤机电动门用
10 | ZRC-DJVVR-2*2*1.0 | 32000 | 电动门指令信号用
11 | ZRC-DJVVP1R-1×3×1.0 | 3000 | 就地控制箱到就地热电阻用
12 | ZRC-DJVVP1R-4×3×1.0 | 580 | 就地控制箱到就地热电阻用
13 | ZRC-DJVVR-12*2*1.0 | 600 | 电接点液位计用
14 | ZRC-KXHFVP-1×2×1.0 | 200 | 就地热电偶到温度变送器用
15 | ZBR-50-220 | 300 | 伴热带
注： （1）使用标准的电缆颜色，维护时可以容易的区分导线的功能，这将使维护更简单 （2）交流导线应遵循下面的颜色规则：相线：红色零线：蓝色接地（PE）：黄绿色 （3）直流导线应遵循下满的颜色规则：正极：棕色负极：黑色接地（IE/PE）：黄绿色 （4）IO模块：本安（IS）：蓝色非本安：绿色安全停车系统（SLE/ESD）：橙色仪表地：黄绿色 （5）仪表电缆5类铜导体，聚氯乙烯绝缘，绝缘层为阻燃材料，屏蔽电缆为镀锡铜丝编织总屏蔽，聚氯乙烯护套阻燃C类计算机电缆，本安24V为兰色/非本安24V为灰色，编织镀锡铜丝总屏蔽，护套颜色： 1）灰色用在非本安上； 2）蓝色用在本安上； 3）橘色用在紧急停车系统；

## 电缆规格颜色
常规电缆标准要求
要求（Requirement）: XLPE交联聚乙烯绝缘，PVC聚氯乙烯护套，阻燃和根据实际情况所作的其它要求（XLPE insulted and an overall sheath of PVC. The overall sheath shall be flame retardant,and other requirements should be considered based on real situation）
项目（Item） | 型号（Type) | 工作温度（Working Temp. Cº） | 环境温度 （Envi. Temp.Cº） | 型号说明 | 其它技术要求（Other Spes.) | 执行标准 | 备注（Remark）
一、仪表电缆(Signal Cable）
1 | ZRC-DJVVP1R 300/500V 2*1.0 | 70 | 40 | 5类铜导体，聚氯乙烯绝缘，绝缘层为阻燃材料，镀锡铜丝编织总屏蔽，聚氯乙烯护套阻燃C类计算机电缆 | 1. 本安24V为兰色/非本安24V为灰色 (Blue for 24V IS/Grey for 24V non IS）2.编织镀锡铜丝总屏蔽 （Collective screen by weaved and tinned copper）3.红黑双色（Red and black color）4.绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement). | TICW 06-2009 、GB/T19666-2005
2 | ZRC-DJVVP1R 300/500V 2*2*1.0 | 70 | 40 | 5类铜导体，聚氯乙烯绝缘，绝缘层为阻燃材料，镀锡铜丝编织总屏蔽，聚氯乙烯护套阻燃C类计算机电缆 | 1. 本安24V为兰色/非本安24V为灰色 (Blue for 24V IS/Grey for 24V non IS）2.铜丝编织镀锡总屏蔽 （Collective screen by weaved and tinned copper）3.黑白双绞线芯加色带及线号 （black and white color for twised pair with color ribbon and core no.mark) 4.绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement). | TICW 06-2009 、GB/T19666-2005
3 | ZRC-DJVVP1R 300/500V 8*2*1.0 | 70 | 40 | 5类铜导体，聚氯乙烯绝缘，绝缘层为阻燃材料，镀锡铜丝编织总屏蔽，聚氯乙烯护套阻燃C类计算机电缆 | 1. 本安24V为兰色/非本安24V为灰色 (Blue for 24V IS/Grey for 24V non IS）2.铜丝编织镀锡总屏蔽 （Collective screen by weaved tinned copper）3.黑白双绞线芯加色带及线号 （black and white color for twised pair with color ribbon and core no. mark)4.绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement). | TICW 06-2009 、GB/T19666-2005
4 | ZRC-DJVVP1R 300/500V 24*2*1.0 | 70 | 40 | 5类铜导体，聚氯乙烯绝缘，绝缘层为阻燃材料，镀锡铜丝编织总屏蔽，聚氯乙烯护套阻燃C类计算机电缆 | 1. 本安24V为兰色/非本安24V为灰色 (Blue for 24V IS/Grey for 24V non IS）2.铜丝编织镀锡总屏蔽 （Collective screen by weaved tinned copper）3.黑白双绞线芯加色带及线号 （black and white color for twised pair with color ribbon and core no. mark)4.绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement). | TICW 06-2009 、GB/T19666-2005
5 | ZRC-KVVP1R 300/500V 3*1.5 | 70 | 40 | 5类铜导体，聚氯乙烯绝缘，绝缘层为阻燃材料，镀锡铜丝编织总屏蔽，聚氯乙烯护套阻燃C类计算机电缆 | 1. 本安24V为兰色/非本安24V为灰色 (Blue for 24V IS/Grey for 24V non IS）2.铜丝编织镀锡总屏蔽 （Collective screen by weaved and tinned copper）3.红，黑，黄绿线芯 （red, black and yellow/green cores ) 4.绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement). | GB/T9330-2008、GB/T19666-2005 | 尽量使用24VDC，避免220VAC 电磁阀(try to use 24VDC solenoide valve and avoid 220VAC type)
6 | ZRC-DJVVR 300/500V 2*1.0 (无屏蔽) | 70 | 40 | 5类铜导体，聚氯乙烯绝缘，绝缘层为阻燃材料，聚氯乙烯护套阻燃C类计算机电缆 | 1. 本安24V为兰色/非本安24V为灰色 (Blue for 24V IS/Grey for 24V non IS）2.红黑双色（Red and black color）3.绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement). | TICW 06-2009 、GB/T19666-2005 | 非屏蔽电缆现用在面/米粉车间-那里绝大部分信号为开关量的
7 | ZRC-DJVVR 300/500V 2*2*1.0 (无屏蔽) | 70 | 40 | 5类铜导体，聚氯乙烯绝缘，绝缘层为阻燃材料，聚氯乙烯护套阻燃C类计算机电缆 | 1. 本安24V为兰色/非本安24V为灰色 (Blue for 24V IS/Grey for 24V non IS）2.黑白双绞线芯加色带及线号 （black and white color for twised pair with color ribbon and no.mark) 3.绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement). | TICW 06-2009 、GB/T19666-2005
8 | ZRC-DJVVR 300/500V 8*2*1.0 (无屏蔽) | 70 | 40 | 5类铜导体，聚氯乙烯绝缘，绝缘层为阻燃材料，聚氯乙烯护套阻燃C类计算机电缆 | 1. 本安24V为兰色/非本安24V为灰色 (Blue for 24V IS/Grey for 24V non IS）2.黑白双绞线芯加色带及线号 （black and white color for twised pair with color ribbon and no.mark) 3.绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement). | TICW 06-2009 、GB/T19666-2005
9 | ZRC-DJVVR 300/500V 24*2*1.0 (无屏蔽) | 70 | 40 | 5类铜导体，聚氯乙烯绝缘，绝缘层为阻燃材料，聚氯乙烯护套阻燃C类计算机电缆 | 1. 本安24V为兰色/非本安24V为灰色 (Blue for 24V IS/Grey for 24V non IS）2.黑白双绞线芯加色带及线号 （black and white color for twised pair with color ribbon and no.mark) 3.绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement). | TICW 06-2009 、GB/T19666-2005
5 | ZRC-KVVR 300/500V 3*1.5 | 70 | 40 | 5类铜导体，聚氯乙烯绝缘，聚氯乙烯护套阻燃C类控制电缆 | 1. 本安24V为兰色/非本安24V为灰色 (Blue for 24V IS/Grey for 24V non IS）2.红，黑，黄绿线芯 （red, black and yellow/green cores ) 3.绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement) | GB/T9330-2008、GB/T19666-2005
二、电机动力电缆 （Motor Power Cable）
1 | ZRC-YJVR 0.6/1kV 4*2.5 | 90 | 40 | 5类铜导体，交联聚乙烯绝缘，聚氯乙烯护套阻燃C类电力电缆电缆 | 黑色护套，线芯分色（black sheath，individual core color);（线芯颜色：黄，绿，红，黄绿） 绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement) | GB/12706.1-2008、GB/T19666-2005 | 为了制作电缆鼻可靠，《6mm²的电缆用YJVR （软线） （in order to make reliable cable shoes, for cable 《6mm², we should use YJVR type
2 | ZRC-YJVR 0.6/1kV 3*4+1*2.5 | 90 | 40 | 5类铜导体，交联聚乙烯绝缘，聚氯乙烯护套阻燃C类电力电缆电缆 | 黑色护套，线芯分色（black sheath，individual core color);（线芯颜色：黄，绿，红，黄绿） 绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement) | GB/12706.1-2008、GB/T19666-2005 | 为了制作电缆鼻可靠，《6mm²的电缆用YJVR （软线） （in order to make reliable cable shoes, for cable 《6mm², we should use YJVR type
3 | ZRC-YJVR 0.6/1kV 3*6+1*4 | 90 | 40 | 5类铜导体，交联聚乙烯绝缘，聚氯乙烯护套阻燃C类电力电缆电缆 | 黑色护套，线芯分色（black sheath，individual core color);（线芯颜色：黄，绿，红，黄绿） 绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement) | GB/12706.1-2008、GB/T19666-2005 | 为了制作电缆鼻可靠，《6mm²的电缆用YJVR （软线） （in order to make reliable cable shoes, for cable 《6mm², we should use YJVR type
4 | ZRC-YJV 0.6/1kV 3*10+1*6 | 90 | 40 | 2类铜导体，交联聚乙烯绝缘，聚氯乙烯护套阻燃C类电力电缆电缆 | 黑色护套，线芯分色（black sheath，individual core color);（线芯颜色：黄，绿，红，黄绿） 绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement) | GB/12706.1-2008、GB/T19666-2005
5 | ZRC-YJV 0.6/1kV 3*16+1*10 | 90 | 40 | 2类铜导体，交联聚乙烯绝缘，聚氯乙烯护套阻燃C类电力电缆电缆 | 黑色护套，线芯分色（black sheath，individual core color);（线芯颜色：黄，绿，红，黄绿） 绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement) | GB/12706.1-2008、GB/T19666-2005
6 | ZRC-YJV 0.6/1kV 3*25+1*16 | 90 | 40 | 2类铜导体，交联聚乙烯绝缘，聚氯乙烯护套阻燃C类电力电缆电缆 | 黑色护套，线芯分色（black sheath，individual core color);（线芯颜色：黄，绿，红，黄绿） 绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement) | GB/12706.1-2008、GB/T19666-2005
7 | ZRC-YJV 0.6/1kV 3*35+1*16 | 90 | 40 | 2类铜导体，交联聚乙烯绝缘，聚氯乙烯护套阻燃C类电力电缆电缆 | 黑色护套，线芯分色（black sheath，individual core color);（线芯颜色：黄，绿，红，黄绿） 绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement) | GB/12706.1-2008、GB/T19666-2005
8 | ZRC-YJV 0.6/1kV 3*50+1*25 | 90 | 40 | 2类铜导体，交联聚乙烯绝缘，聚氯乙烯护套阻燃C类电力电缆电缆 | 黑色护套，线芯分色（black sheath，individual core color);（线芯颜色：黄，绿，红，黄绿） 绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement) | GB/12706.1-2008、GB/T19666-2005
9 | ZRC-YJV 0.6/1kV 3*70+1*35 | 90 | 40 | 2类铜导体，交联聚乙烯绝缘，聚氯乙烯护套阻燃C类电力电缆电缆 | 黑色护套，线芯分色（black sheath，individual core color);（线芯颜色：黄，绿，红，黄绿） 绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement) | GB/12706.1-2008、GB/T19666-2005
10 | ZRC-YJV 0.6/1kV 3*95+1*50 | 90 | 40 | 2类铜导体，交联聚乙烯绝缘，聚氯乙烯护套阻燃C类电力电缆电缆 | 黑色护套，线芯分色（black sheath，individual core color);（线芯颜色：黄，绿，红，黄绿） 绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement) | GB/12706.1-2008、GB/T19666-2005
11 | ZRC-YJV 0.6/1kV 3*120+1*70 | 90 | 40 | 2类铜导体，交联聚乙烯绝缘，聚氯乙烯护套阻燃C类电力电缆电缆 | 黑色护套，线芯分色（black sheath，individual core color);（线芯颜色：黄，绿，红，黄绿） 绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement) | GB/12706.1-2008、GB/T19666-2005
12 | ZRC-YJV 0.6/1kV 3*185+1*95 | 90 | 40 | 2类铜导体，交联聚乙烯绝缘，聚氯乙烯护套阻燃C类电力电缆电缆 | 黑色护套，线芯分色（black sheath，individual core color);（线芯颜色：黄，绿，红，黄绿） 绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement) | GB/12706.1-2008、GB/T19666-2005
13 | ZRC-YJV 0.6/1kV 3*240+1*120 | 90 | 40 | 2类铜导体，交联聚乙烯绝缘，聚氯乙烯护套阻燃C类电力电缆电缆 | 黑色护套，线芯分色（black sheath，individual core color);（线芯颜色：黄，绿，红，黄绿） 绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement) | GB/12706.1-2008、GB/T19666-2005
三、动力分配电缆（Power Distribution）
1 | ZRC-YJVR 0.6/1kV 5*2.5 | 90 | 40 | 5类铜导体，交联聚乙烯绝缘，聚氯乙烯护套阻燃C类电力电缆电缆 | 黑色护套，线芯分色（black sheath，individual core color);（线芯颜色：黄，绿，红，蓝，黄绿） 绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement) | GB/12706.1-2008、GB/T19666-2005 | 为了制作电缆鼻可靠，《6mm²的电缆用YJVR （软线） （in order to make reliable cable shoes, for cable 《6mm², we should use YJVR type
2 | ZRC-YJVR 0.6/1kV 4*4+1*2.5 | 90 | 40 | 5类铜导体，交联聚乙烯绝缘，聚氯乙烯护套阻燃C类电力电缆电缆 | 黑色护套，线芯分色（black sheath，individual core color);（线芯颜色：黄，绿，红，蓝，黄绿） 绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement) | GB/12706.1-2008、GB/T19666-2005 | 为了制作电缆鼻可靠，《6mm²的电缆用YJVR （软线） （in order to make reliable cable shoes, for cable 《6mm², we should use YJVR type
3 | ZRC-YJVR 0.6/1kV 4*6+1*4 | 90 | 40 | 5类铜导体，交联聚乙烯绝缘，聚氯乙烯护套阻燃C类电力电缆电缆 | 黑色护套，线芯分色（black sheath，individual core color);（线芯颜色：黄，绿，红，蓝，黄绿） 绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement) | GB/12706.1-2008、GB/T19666-2005 | 为了制作电缆鼻可靠，《6mm²的电缆用YJVR （软线） （in order to make reliable cable shoes, for cable 《6mm², we should use YJVR type
4 | ZRC-YJV 0.6/1kV 4*10+1*6 | 90 | 40 | 2类铜导体，交联聚乙烯绝缘，聚氯乙烯护套阻燃C类电力电缆电缆 | 黑色护套，线芯分色（black sheath，individual core color);（线芯颜色：黄，绿，红，蓝，黄绿） 绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement) | GB/12706.1-2008、GB/T19666-2005
5 | ZRC-YJV 0.6/1kV 4*16+1*10 | 90 | 40 | 2类铜导体，交联聚乙烯绝缘，聚氯乙烯护套阻燃C类电力电缆电缆 | 黑色护套，线芯分色（black sheath，individual core color);（线芯颜色：黄，绿，红，蓝，黄绿） 绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement) | GB/12706.1-2008、GB/T19666-2005
6 | ZRC-YJV0.6/1kV 4*25+1*16 | 90 | 40 | 2类铜导体，交联聚乙烯绝缘，聚氯乙烯护套阻燃C类电力电缆电缆 | 黑色护套，线芯分色（black sheath，individual core color);（线芯颜色：黄，绿，红，蓝，黄绿） 绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement) | GB/12706.1-2008、GB/T19666-2005
7 | ZRC-YJV 0.6/1kV 4*35+1*16 | 90 | 40 | 2类铜导体，交联聚乙烯绝缘，聚氯乙烯护套阻燃C类电力电缆电缆 | 黑色护套，线芯分色（black sheath，individual core color);（线芯颜色：黄，绿，红，蓝，黄绿） 绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement) | GB/12706.1-2008、GB/T19666-2005
8 | ZRC-YJV 0.6/1kV 4*50+1*25 | 90 | 40 | 2类铜导体，交联聚乙烯绝缘，聚氯乙烯护套阻燃C类电力电缆电缆 | 黑色护套，线芯分色（black sheath，individual core color);（线芯颜色：黄，绿，红，蓝，黄绿） 绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement) | GB/12706.1-2008、GB/T19666-2005
9 | ZRC-YJV 0.6/1kV 4*70+1*35 | 90 | 40 | 2类铜导体，交联聚乙烯绝缘，聚氯乙烯护套阻燃C类电力电缆电缆 | 黑色护套，线芯分色（black sheath，individual core color);（线芯颜色：黄，绿，红，蓝，黄绿） 绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement) | GB/12706.1-2008、GB/T19666-2005
10 | ZRC-YJV 0.6/1kV 4*95+1*50 | 90 | 40 | 2类铜导体，交联聚乙烯绝缘，聚氯乙烯护套阻燃C类电力电缆电缆 | 黑色护套，线芯分色（black sheath，individual core color);（线芯颜色：黄，绿，红，蓝，黄绿） 绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement) | GB/12706.1-2008、GB/T19666-2005
11 | ZRC-YJV 0.6/1kV 4*120+1*70 | 90 | 40 | 2类铜导体，交联聚乙烯绝缘，聚氯乙烯护套阻燃C类电力电缆电缆 | 黑色护套，线芯分色（black sheath，individual core color);（线芯颜色：黄，绿，红，蓝，黄绿） 绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement) | GB/12706.1-2008、GB/T19666-2005
12 | ZRC-YJV 0.6/1kV 4*185+1*95 | 90 | 40 | 2类铜导体，交联聚乙烯绝缘，聚氯乙烯护套阻燃C类电力电缆电缆 | 黑色护套，线芯分色（black sheath，individual core color);（线芯颜色：黄，绿，红，蓝，黄绿） 绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement) | GB/12706.1-2008、GB/T19666-2005
13 | ZRC-YJV 0.6/1kV 4*240+1*120 | 90 | 40 | 2类铜导体，交联聚乙烯绝缘，聚氯乙烯护套阻燃C类电力电缆电缆 | 黑色护套，线芯分色（black sheath，individual core color);（线芯颜色：黄，绿，红，蓝，黄绿） 绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement) | GB/12706.1-2008、GB/T19666-2005
四、电机控制电缆 （Motor Control）
1 | ZRC-KYJVR 0.6/1kV 5*1.5 | 90 | 40 | 5类铜导体，交联聚乙烯绝缘，聚氯乙烯护套阻燃C类控制电缆电缆 | 黑色护套，线芯分色（black sheath，individual core color); 绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement) | GB/T9330-2008、GB/T19666-2005
2 | ZRC-KYJVR 0.6/1kV 6*1.0 | 90 | 40 | 5类铜导体，交联聚乙烯绝缘，聚氯乙烯护套阻燃C类控制电缆电缆 | 黑色护套，线芯分色（black sheath，individual core color); 绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement) | GB/T9330-2008、GB/T19666-2005
五、照明电缆（Lighting）
1 | ZRC-YJVR 0.6/1kV3*2.5 | 90 | 40 | 2类铜导体，交联聚乙烯绝缘，聚氯乙烯护套阻燃C类电力电缆电缆 | 黑色护套，线芯分色（black sheath，individual core color); 绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement) | GB/12706.1-2008、GB/T19666-2005 | 为了制作电缆鼻可靠，《6mm²的电缆用YJVR （软线） （in order to make reliable cable shoes, for cable 《6mm², we should use YJVR type
2 | ZRC-YJVR 0.6/1kV3*4 | 90 | 40 | 2类铜导体，交联聚乙烯绝缘，聚氯乙烯护套阻燃C类电力电缆电缆 | 黑色护套，线芯分色（black sheath，individual core color); 绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement) | GB/12706.1-2008、GB/T19666-2005 | 为了制作电缆鼻可靠，《6mm²的电缆用YJVR （软线） （in order to make reliable cable shoes, for cable 《6mm², we should use YJVR type
3 | ZRC-YJV 0.6/1kV 4*10+1*6 | 90 | 40 | 2类铜导体，交联聚乙烯绝缘，聚氯乙烯护套阻燃C类电力电缆电缆 | 黑色护套，线芯分色（black sheath，individual core color)（线芯颜色：黄，绿，红，蓝，黄绿）; 绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement) | GB/12706.1-2008、GB/T19666-2005
4 | ZRC-YJV22 0.6/1kV 4*16+1*10 | 90 | 40 | 2类铜导体，交联聚乙烯绝缘，钢带铠装，聚氯乙烯护套阻燃C类电力电缆电缆 | 黑色护套，线芯分色（black sheath，individual core color)（线芯颜色：黄，绿，红，蓝，黄绿）; 绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement) | GB/12706.1-2008、GB/T19666-2005
六、高中压供电电缆（H/M Voltage cable）
1 | ZRA-YJV22 8.7/15kV 3*120 | 90 | 40 | 2类铜导体，交联聚乙烯绝缘，钢带铠装，聚氯乙烯护套阻燃A类电力电缆电缆 | 黑色护套，线芯分色（black sheath，individual core color); 绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement) | GB/12706.2-2008、GB/T19666-2005
2 | ZRA-YJV22 8.7/15kV 3*120 | 90 | 40 | 2类铜导体，交联聚乙烯绝缘，钢丝铠装，聚氯乙烯护套阻燃A类电力电缆电缆 | 黑色护套，线芯分色（black sheath，individual core color); 绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement) | GB/12706.2-2008、GB/T19666-2005 | 用在海水腐蚀较大的工况（suitable for seawater erosive area)
3 | ZRA-YJV22 18/30kV 3*120 | 90 | 40 | 2类铜导体，交联聚乙烯绝缘，钢带铠装，聚氯乙烯护套阻燃A类电力电缆电缆 | 黑色护套，线芯分色（black sheath，individual core color); 绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement) | GB/12706.2-2008、GB/T19666-2005
4 | ZRA-YJV22 26/35kV 3*120 | 90 | 40 | 2类铜导体，交联聚乙烯绝缘，钢带铠装，聚氯乙烯护套阻燃A类电力电缆电缆 | 黑色护套，线芯分色（black sheath，individual core color); 绝缘和护套的厚度不应该小于国标的标称厚度（insulation/jacket layer's thickness should be not less than GB's nominal requirement) | GB/12706.2-2008、GB/T19666-2005
备注Note:
1）不得有任何修补或接头，所有的填料都应为使用阻燃材料；
2）生产商必须符合地方性法规/标准
ZR: 阻燃（Fire retardant）(ZR或ZC：阻燃C类 ZA：阻燃A类);
DJ: 计算机电缆，测量用对绞电缆 （For computer and measurement twisted cable)
YJ:交联聚乙烯（XLPE）
V:聚氯乙烯（PVC）
P: 屏蔽（Screened，C in German standard)（P:编织屏蔽 P1:镀锡铜丝编织屏蔽）
R: 软线 （more threads in one core， Li German standard)
K: 控制（control)
22: 铠装（SWA，Qb in German standard)（钢带铠装+外护套为聚氯乙烯）
YJV23:铠装+XLPE绝缘+外护套为聚乙烯 (SWA+XLPE insulation+PE sheath)
紧急停车系统的电缆用橙色Orange color for 24V ESD cable
施工温度应在0°C以上，寒冷地区可考虑耐寒型电缆(YJV cable should be installed above 0°C degree)